## Worksheet
LOGBOOK SYSTEM
Unit | Main Category | Sub System | Date/Time Performed | Date Done | Done By | Due Date | Notes | Performed By | Logged By | Logged Date | Status
|  |  | 2021-02-25 09:00 | 2021-03-10 00:11:00 |  |  | 1. Removed wire wound resistor and connect AVR output directly across exciter field. 2. Replaced AVR power fuse with miniature circuit breaker. 3. Adjusted settings: a. Under voltage 3= 85% at 3s b. Loss of Excitation= 20% at 1s 4. Adjusted Voltage stability and sensibility settings 5. Test run DG#2 6. For close monitoring and observation. Parts replacement: 1.) 1 pair miniature circuit breaker 2P, 10A | J.Abrio, I. Medora, J.Z.Delica, J.Limuran, M. Metrio |  | 2021-02-25 15:09:27 | Done
|  |  | 2021-02-26 7:15 | 2021-02-26 08:32:17 |  | 2021-02-26 | Scope of Work 1.) Rectify the Starting Air Pressure due to high pressure. Actions taken by Mechanical team: 1. Re-adjust regulator for Starting Air before Air Motor. a.) Set @ 8.1 BARS in Control Panel Room b.) Replace gauge due to inaccuracy Replacement of Parts a.) 1 pc Gauge taken from Container Van No. 5 | J. Quilang |  | 2021-02-26 08:32:17 | Done
|  |  | 2021-02-26 7:00 | 2021-03-07 23:38:20 |  |  | 1.) Start Main Bearing Installation a.) main Bearing No. 2 | R. Radaza, J. Agoncillo, J. Quilang, W. Bequilla, J. Jaraza |  | 2021-02-26 10:22:55 | Done
|  |  | 2021-02-26 7:00 | 2021-02-26 10:35:38 |  | 2021-02-26 | 1.) Level Switch installation at DG#1 sump tank. | I. Medora |  | 2021-02-26 10:35:38 | Done
|  |  | 2021-02-26 7:00 | 2021-02-26 10:55:23 |  |  | 1.) Installation of Effluent Flow Meter at the oily water separator discharge. | N. Beato |  | 2021-02-26 10:55:23 | Done
UPDATES: |  |  | 2021-02-27 7:00 |  |  |  | 1.) Installation of Effluent Flow Meter at the oily water separator discharge. | N. Beato, J. Agoncillo |  | 2021-02-27 15:24:38 | Done
|  |  | 2021-02-27 7:00 | 2021-02-27 08:36:15 |  | 2021-02-27 | 1.) Replaced non working Pressure Gauge at Gauge Panel for Fuel Oil Pressure to working spare Pressure Gauge. (0-10 bar) | I. Medora, J. Delica |  | 2021-02-27 08:36:15 | Done
|  |  | 2021-02-27 2:30 | 2021-02-27 15:41:35 |  | 2021-02-27 | 1.) Simulation and Testing of Protection Relay at 23MH4 Switchgear by ASIA PHIL. | Angelo Dayao, Renan Bacatan |  | 2021-02-27 15:41:35 | Done
UPDATES: |  |  | 2021-02-27 2:30 |  |  |  | 1.) Simulation and Testing of Protection Relay at 23MH4 Switchgear by ASIA PHIL | Angelo Dayao, Renan Bacatan |  | 2021-02-27 16:29:19 | Done
|  |  | 3:30 | 2021-02-27 16:27:53 |  | 2021-02-27 | 1.) Wiring for the HT temp alarm. | I. Medora, J. Delica |  | 2021-02-27 15:44:56 | Done
|  |  | 2021-02-28 7:00 | 2021-02-28 13:11:03 |  | 2021-02-28 | 1.)Install Pressure Gauges (2 nos.) & Thermometer (1 pc.) at the L.O. Purifier system. | I. Medora, J. Delica |  | 2021-02-28 13:11:03 | Done
|  |  | 2021-03-05 08:00 | 2021-03-15 10:32:24 |  |  | Reconditioning of cylinder heads | Maintenance team, CLB |  | 2021-03-05 13:10:59 | Done
UPDATES: |  |  | 2021-03-10 07:30 |  |  |  | Installation of cylinder heads | Maintenance team |  | 2021-03-10 08:10:56 | On-Progress
|  |  | 2021-03-05 08:00 | 2021-03-07 08:20:40 |  |  | Installation of pistons | Maintenance team, CLB |  | 2021-03-05 13:12:16 | Done
|  |  | 2021-03-05 08:00 | 2021-04-04 16:53:41 |  |  | Wiring installation of signal cables | I. Medora |  | 2021-03-05 13:14:04 | Done
|  |  | 2021-03-08 07:30 | 2021-03-08 09:23:54 |  |  | Replaced cylinder head no. 4 due to water leaks found during air run. | Maintenance team |  | 2021-03-08 09:23:54 | Done
UPDATES: |  |  | 2021-03-08 13:30 |  |  |  | Conducted air run after replacement of cylinder no. 4 completed. | 1st Shift Operators |  | 2021-03-08 13:32:56 | Done
|  |  | 2021-03-09 08:00 | 2021-06-22 15:08:10 |  |  | Servicing of LO Separator bowl assembly due to frequent abnormal sludging. | J. Quilang & J. Lastica |  | 2021-03-09 10:08:39 | Done
|  |  | 2021-03-09 11:44 | 2021-03-09 13:40:58 |  | 2021-03-09 | Adjusted AVR Stability setting from 45% to 25% performed by PETCO (James). | PETCO (James) |  | 2021-03-09 13:40:58 | Done
|  |  | 2021-02-25 9:00 | 2021-03-10 00:16:19 |  |  | 1.Â Â Removed wire wound resistor and connect AVR output directly across exciter field. 2. Replaced AVR power fuse with miniature circuit breaker. 3. Adjusted settings: a. Under voltage 3= 85% at 3s b. Loss of Excitation= 20% at 1s 4. Adjusted Voltage stability and sensibility settings 5. Test run DG#2 6. For close monitoring and observation. Parts replacement: 1.) 1 pair miniature circuit breaker 2P, 10A | J.Abrio, I. Medora, J.Z.Delica, J.Limuran, M. Metrio |  | 2021-03-10 00:16:19 | Done
|  |  | 2021-02-25 9:00 | 2021-03-10 00:19:26 |  |  | 1.Â Â Removed wire wound resistor and connect AVR output directly across exciter field. 2. Replaced AVR power fuse with miniature circuit breaker. 3. Adjusted settings: a. Under voltage 3= 85% at 3s b. Loss of Excitation= 20% at 1s 4. Adjusted Voltage stability and sensibility settings 5. Test run DG#2 6. For close monitoring and observation. Parts replacement: 1.) 1 pair miniature circuit breaker 2P, 10A | J.Abrio, I. Medora, J.Z.Delica, J.Limuran, M. Metrio |  | 2021-03-10 00:19:26 | Done
|  |  | 2021-03-12 09:00 | 2021-03-12 13:17:33 |  | 2021-03-12 | Inspection / Rectification of DG3 Lube Oil Pump due to abnormal sound while in operation. | Mechanical Team |  | 2021-03-12 13:17:33 | Done
UPDATES: |  |  | 2021-04-07 00:00 |  |  |  | Replaced bearing | Maintenance team |  | 2021-04-07 06:53:29 | Done
|  |  | 2021-03-15 07:30 | 2021-03-15 12:32:19 |  | 2021-03-15 | Servicing of Engine Fuel Pressure Switch. | J. Delica |  | 2021-03-15 12:32:19 | Done
|  |  | 2021-03-15 07:30 | 2021-03-15 12:35:23 |  | 2021-03-15 | Servicing of Booster Module-2: -Dewatering of mixing tank -Air bleeding of the system | 1st Shift Operators |  | 2021-03-15 12:35:23 | Done
|  |  | 2021-03-15 07:30 | 2021-03-15 14:43:57 |  |  | Re-activation of Viscosity controller at Booster Module-1 Heater is controlled by viscosity. Settings as follows: SP=15cst Max=18cst Min=10cst | DM Contractor & EIC Team |  | 2021-03-15 12:40:49 | Done
|  |  | 2021-03-15 07:00 | 2021-03-16 09:56:12 |  | 2021-03-15 | March 15, 2021 0700H-1600H Activities: â€¢ Headers connections and accessory lines installation for fuel, start air , noozle cooling , rocker arm lubrication and leak-off pipes is done. Subject for leak-testing â€¢ Rectification and adjustments of fuel linkage , rack and governor set to zero. â€¢ Dismantle and cleaning of noozle cooling filter and rocker arm lubrication filter then installed back. | JJ,NB,WB,MR,JL,JQ |  | 2021-03-16 09:56:12 | Done
|  |  | 2020-12-25 07:00 | 2021-03-29 08:56:04 |  |  | DEC 25 , 2020 â€“ 0700H-1600H ACTIVITIES: â€¢ FABRICATE TRASH BIN BASE FRAME â€¢ INSTALLED NEW ORING FOR EXHAUST VALVE CAGE CW. PATH (8DK-32) â€¢ AUXILIARY EQUIPMENTS MONITORING | NESTOR BEATO, JAY QUILANG |  | 2021-03-29 08:56:04 | Done
|  |  | 2021-04-04 07:30 | 2021-04-04 16:57:03 |  | 2021-04-04 | Replaced FIP no. 6 due to minimal fuel leak. | J. Jaraza & J. Lastica |  | 2021-04-04 16:57:03 | Done
|  |  | 2021-04-14 07:00 | 2021-04-15 09:40:20 |  | 2021-04-14 | Activities : 1. Replaced FIP Newly Reconditioned Spare @ Cyl. 1 due to fuel leak. 2. Reco, Assembled FIP , 1 pc from DG4 Cyl. 1 to be used as spare. 3. Housekeeping @ work area. | NB, JJ, JA, MR |  | 2021-04-15 09:40:20 | Done
|  |  | 2021-04-14 07:00 | 2021-04-15 09:57:08 |  | 2021-04-14 | Activities: 1.Push Rod sleeves for cylinders 4,5,6 & 8 has been rectified. 2.T/C Bello (after) fastening bolts and nuts completed & all re-tightened. 3. Housekeeping | Jason Lastica, Jay Quilang |  | 2021-04-15 09:57:08 | Done
|  |  | 2021-04-14 07:00 | 2021-04-15 10:31:04 |  | 2021-04-14 | Activities: 1. 1 unit cylinder head from India Has been modified & made as spare. 2. Engine Monitoring. | Jason Lastica, Jay Quilang |  | 2021-04-15 10:31:04 | Done
UPDATES: |  |  | : | [6 empty] | 2021-04-15 10:31:29 | Done
|  |  | 2021-04-14 07:00 | 2021-04-15 13:34:50 |  | 2021-04-14 | Activities: 1. Monitoring Generator Parameters or temperatures of motors panels, and switches. 2. Inspection of DG4 Diode & Surge Suprressor. 3. Inspect DG4 Control Panel. 4. Housekeeping. | EIC Team, Ian Medora, Jaylord Delica |  | 2021-04-15 13:34:50 | Done
|  |  | 2021-04-15 07:00 | 2021-04-17 14:21:54 |  | 2021-04-15 | Activities: 1. Repair of Warehouse Extension - Container Van. | JA, JJ, WB , MR |  | 2021-04-17 14:21:54 | Done
|  |  | 2021-04-16 07:00 | 2021-04-17 14:25:03 |  | 2021-04-17 | Activities: 1. Modification & Making cylinder head spare from those extra ones coming from India. - on going process 2. Continuation on Container Van works - warehouse extension 3. Monitoring of leaks on engine 1 and 2 online for dispatch . |  |  | 2021-04-17 14:25:03 | Done
UPDATES: |  |  | : | [6 empty] | 2021-04-19 13:19:19 | Done
|  |  | 2021-04-15 07:00 | 2021-04-17 14:29:46 |  | 2021-04-15 | Activities: 1. Pull-out Erosion Plug in Cylinder #1 due to fuel leakage . . Replaced Erosion plug and new copper gasket in Cylinder No.1 3. Monitoring of Running Engine. 4. Housekeepin | JJ,WB,JA, MR |  | 2021-04-17 14:29:46 | Done
|  |  | 2021-04-17 07:00 | 2021-04-19 14:43:25 |  | 2021-04-18 | Activties: 1. Retightening of Exhaust Manifold bolt due to leak on Cyl. 6 , 7 and 8 already tighten and done. 2.. Pull out exhaust cladding to visualized leakage , abnormalities found broken gasket and loosen bolt subject for replacement of gasket. 3. Housekeeping | John Jarasa |  | 2021-04-19 14:43:25 | Done
|  |  | 2021-04-18 07:00 | 2021-04-19 14:47:53 |  | 2021-04-18 | Activities: 1. Horinzontal Bellow after T/C Leaked (exhaust) rectified & installed with made gasket. 2. Re-tightened exhaust valve cage for Cyl. 5&6 to a torque of 180 N.M 3. Fabricated & Installed modified fuel -leak off connection pipe going to leak-off storage tank. | NB, WB, JA, JL, JQ |  | 2021-04-19 14:47:53 | Done
|  |  | 2021-04-18 15:00 | 2021-04-19 14:50:53 |  | 2021-04-18 | Activities: 1. Retightening of exhaust bolt after turbo with the use of washer due to leak , tightening done. 2. Housekeeping | John Jarasa |  | 2021-04-19 14:50:53 | Done
|  |  | 2021-04-19 07:00 | 2021-04-22 15:52:43 |  | 2021-04-19 | Activities: 1. Modified another cylinder head from india ut incomplete and not fully done reassembling due to none availability of some parts needed. | NB,WB,MR,JL,JQ |  | 2021-04-22 15:52:43 | Done
|  |  | 2021-04-20 07:00 | 2021-04-22 15:56:35 |  | 2021-04-20 | Activities: 1. Installed back remove cladding at HFO line going to DG1. 1. Installed back remove clading at DG1 leak off line. | JL, NB, WB,MR |  | 2021-04-22 15:56:35 | Done
|  |  | 2021-04-21 07:00 | 2021-04-22 16:06:48 |  | 2021-04-22 | Actiivities: 1. Recondition and Assessment of another cylinder head from India to be prepared for spare. | NB, MR, JJ, JL, JQ |  | 2021-04-22 16:06:48 | Done
|  |  | 2021-04-15 07:00 | 2021-04-30 14:11:24 |  | 2021-04-15 | Activities: 1. Adjustment and monitoring of AVR response at DG4. 2. Functionality Test of under voltage relay and under frequency relay at auxiliary panel DG1. | EIC Team, Ian Medora, Jaylord Delica |  | 2021-04-30 14:11:24 | Done
|  |  | 2021-04-16 07:00 | 2021-04-30 14:12:56 |  | 2021-04-16 | Activities: 1. Uninstall AVR at DG4 and transfer to DG3 for testing and further evaluation. | EIC Team, Ian Medora, Jaylord Delica |  | 2021-04-30 14:12:56 | Done
|  |  | 2021-04-17 07:00 | 2021-04-30 14:14:36 |  | 2021-04-17 | Activities: 1. Change generator filter DG2. 2. Remove and replace power fuse lighting | EIC Team, Ian Medora, Jaylord Delica |  | 2021-04-30 14:14:36 | Done
|  |  | 2021-04-18 07:00 | 2021-04-30 14:16:33 |  | 2021-04-18 | Activities: 1. Install posing relay for additional interlock of heater at booster module #1. 2. Monitor | EIC Team, Ian Medora, Jaylord Delica, Abrio |  | 2021-04-30 14:16:33 | Done
|  |  | 2021-04-19 07:00 | 2021-04-30 14:17:57 |  | 2021-04-19 | Activities: 1. Cleaning / Dusting DG4 Control Panel ; cleaning DG4 Engine side 2. monitoring | EIC Team, Ian Medora, Jaylord Delica, Jashoer Abrio |  | 2021-04-30 14:17:57 | Done
|  |  | 2021-04-22 07:00 | 2021-04-30 14:19:46 |  | 2021-04-22 | Activities: 1. Additional wiring of control and alarm of blackstart auto start and reset 2. monitoring |  |  | 2021-04-30 14:19:46 | Done
|  |  | 2021-04-22 07:00 | 2021-04-30 14:36:01 |  | 2021-04-22 | Activities: 1. HFO Purifier #1 & 2 bowl parts inspection & trouble shooting , due to abnormal operation / no separation. -re-adjust both gear pump adjusting screw w/o lock nut to 13.7 mm. -replace both safety joints(broken) -purifier #2 on going troubleshooting (bowl switch 1&2) -#1 is OK, now in separation process | NB, WB, JL, JJ, MR, JQ |  | 2021-04-30 14:36:01 | Done
|  |  | 2021-05-18 10:00 | 2021-05-21 14:34:07 |  | 2021-05-20 | DG2 undergo standard 2k PMS | Maintenance team, Elecl, and Operations |  | 2021-05-21 14:34:07 | Done
|  |  | 2021-06-22 11:00 | 2021-07-04 11:49:10 |  |  | -DG3 undergo CMS due to tiny crack at gas inlet casing. -Repair turbocharger gas inlet casing (welding works) | Maintenance team |  | 2021-06-22 15:07:32 | Done
|  |  | 2021-07-04 10:00 | 2021-07-13 16:49:27 |  |  | Bowl servicing of DG3 LO Separator | Jay Quilang |  | 2021-07-04 11:50:57 | Done
|  |  | 2021-07-13 15:30 | 2021-07-13 16:53:09 |  | 2021-07-13 | Replaced LO filters due to low LO pressure readings (only 3.5 Bars at engine panel). Note: LO filters installed was taken from DG5 | Warren Bequilla and Nestor Beato |  | 2021-07-13 16:53:09 | Done
|  |  | 2021-07-13 15:30 | 2021-07-13 16:55:55 |  | 2021-07-13 | LO filter swap to DG2 due to low LO pressure readings of DG2. Note: See DG2 logbook with same date and time. | Warren Bequilla and Nestor Beato |  | 2021-07-13 16:55:55 | Done
|  |  | 2021-07-21 07:00 | 2021-07-21 11:34:21 |  | 2021-07-21 | 1. Replaced cyl. no.3 due to gas cutting of exhaust valve. 2.Performed standard 500RH PMS both mechanical land electrical. | Maintenance and EIC |  | 2021-07-21 11:34:21 | Done
|  |  | 2021-07-15 : | 2021-07-28 05:18:02 |  | 2021-07-15 | Replacement of cylinder head no.1 due to Gas cutting | Maintenance team |  | 2021-07-28 05:18:02 | Done
|  |  | 2021-07-25 : | 2021-07-28 05:19:41 |  | 2021-07-25 | Replacement of cylinder head no.8 due to Gas cutting | Maintenance team |  | 2021-07-28 05:19:41 | Done
|  |  | 2021-07-27 07:00 | 2021-08-11 13:47:12 |  |  | Replacement of cylinder head no.8 due to broken valve yolks and defective r-side push rod | Maintenance team |  | 2021-07-28 05:24:36 | Done
|  |  | 2021-08-10 23:29 | 2021-08-11 13:50:38 |  | 2021-08-11 | Pull-out cylinder head No.3 due to gas cut, then replaced with reconditioned spare cylinder head assy. | Maintenance team |  | 2021-08-11 13:50:38 | Done
|  |  | 2021-08-10 13:00 | 2021-08-11 13:55:45 |  | 2021-08-10 | Performed repair of turbocharger gas inlet casing due to gas leaks and cracks found. Repair using the welding method led by Sir Edwin. | ECMG Turbo Charger Group |  | 2021-08-11 13:55:45 | Done
|  |  | 2021-08-10 07:00 | 2021-08-11 14:00:13 |  | 2021-08-10 | 1. Replacement of charge air cooler. 2. Replacement of LT & HT thermostatic valves. | Maintenance team |  | 2021-08-11 14:00:13 | Done
|  |  | 2021-08-09 07:00 | 2021-08-12 14:43:19 |  | 2021-08-09 | Pull-out cylinder head nos. 3,4, and 5 | Maintenance team |  | 2021-08-12 14:43:19 | Done
|  |  | 2021-08-09 07:00 | 2021-08-12 14:45:26 |  | 2021-08-09 | Pull-out piston Nos. 3, 4, and 5. | Maintenance team |  | 2021-08-12 14:45:26 | Done
|  |  | 2021-08-09 07:00 | 2021-08-12 14:47:12 |  | 2021-08-09 | Pull-out Conrad and big-end bearing of cylinder nos.3, 4, and 5. | Maintenance team |  | 2021-08-12 14:47:12 | Done
|  |  | 2021-08-09 07:00 | 2021-08-12 14:48:39 |  | 2021-08-09 | Pull-out Main bearing nos. 4 and 5 and replaced old bearing in lower side. | Maintenance team |  | 2021-08-12 14:48:39 | Done
|  |  | 2021-08-09 07:00 | 2021-08-12 14:51:01 |  | 2021-08-09 | Removed thrust bearing both turbo side and generator side | Maintenance team |  | 2021-08-12 14:51:01 | Done
|  |  | 2021-08-12 07:00 | 2021-08-12 14:53:43 |  | 2021-08-12 | Servicing of DG3 LO separator. -Completed/Put back in service. | Jay Quilang |  | 2021-08-12 14:53:43 | Done
|  |  | 2021-08-30 : | 2021-09-01 03:01:06 |  | 2021-08-30 | Replacement of rubber coupling at flywheel side. Notes: *Replacement parts was taken from Calapan power. MHEC PR for this with ref#:PR-MHEC-2021-055 still to follow-up. *Refer to DG1 Incident Report dated Aug. 29, 2021 *Refer to Damage Report Ref#: DR-MHEC2021-009 | Maintenance team |  | 2021-09-01 03:01:06 | Done
|  |  | 2021-09-04 : | 2021-09-04 11:05:23 |  | 2021-09-04 | Standard 3000RH PMS. -Also pull-out and replaced 3 injection pumps and injectors. -Conducted internal & external engine inspection. -cleaning of fuel oil filters at the engine side. -change the oil of generator bearing and governor. -conducted Electrical PMS to generator and control room control panels. | Operation Maintenance and EIC personnel |  | 2021-09-04 11:05:23 | Done
|  |  | 2021-09-06 07:30 | 2021-09-06 14:09:08 |  | 2021-09-06 | Cleaning/servicing of DG2 LO Separator. Note: As-found, plenty of dirt/carbons inside the bowl. | Jay Quilant and Mark Ramos |  | 2021-09-06 14:09:08 | Done
|  |  | 2021-09-07 07:30 | 2021-09-08 07:41:58 |  | 2021-09-07 | Cleaning/servicing of HFO Purifier-1 | Maintenance team |  | 2021-09-08 07:41:58 | Done
|  |  | 2021-09-07 07:30 | 2021-09-08 07:43:46 |  | 2021-09-07 | Cleaning/servicing of DG3 LO Separator | Maintenance team |  | 2021-09-08 07:43:46 | Done
|  |  | 2021-09-19 16:10 | 2022-01-20 16:38:34 |  |  | Annealing of crankpin no.4 performed by G.U. Eng'g. | GU Engineering |  | 2021-09-19 22:30:18 | Done
|  |  | 2020-12-01 23:00 | 2022-01-20 11:25:17 |  |  | ACTIVITIES: 2320H CHANGE OVER HFO FILTER OF BOOSTER MODULE #1 0600H LO SOUNDING 31.5 CM (1321.5L) ENGINE ONLINE LO SEPARATOR OFFLINE ABNORMALITIES: LO LEAKS ON CRANK CASE RELIEF VALVE #4 LO LEAK ON LO PRESSURE GAUGE FITTING JW IN TEMP. GAUGE IS BLURRED JW OUT MONITOR AT THE CONTROL ROOM IS NOT ACCURATE ALWAYS CHECK JW TEMP AT THE ENGINE | MANPOWER: EO- LINGA AO-MENDOZA, CALDERON CRO- VALDEZ SS- PANGAN |  | 2022-01-20 11:25:17 | Done
|  |  | 2021-01-01 07:00 | 2022-01-27 13:58:30 |  | 2021-01-01 | DATE: JANUARY 01, 2021 MANPOWER: EO- VILLANUEVA AO- CALDERON, RAMOS CRO- VALDEZ 0700H ENGINE ON STANDBY 1330H LO OSUNDING 27.7 CM (1144.8L) ENGINE OFFLINE LO SEPARATOR ONLINE LO PRIMING ONLINE DATE: JANUARY 01, 2021 MANPOWER: EO- ORNEDO AO-LEUTERIO CRO-ANYAYAHAN SS-OLAGUER ACTIVITIES: 1500H ENGINE IS ON STANDBY : WAITING FOR DISPATCH 1503H PREPARE 1 DRUM OF LUBE OIL SHELL ARGINA S4 : SAE40 LOCAL â€“ IN CASE OF TOP UP DUE TO LOW ENGINE SUMP LEVEL 1800H SOUNDING 27.5CM(1188L) ENGINE OFFLINE LO SEPARATOR AND HEATER OFFLINE LO PRIMING ONLINE DATE: JANUARY 01-02, 2021 MANPOWER: EO-DEVILLA, LINGA AO-MENDOZA,BANASTAS CRO-MASCULINO SS-PANGAN ACTIVITIES: ENGINE BARIRNG AND EXERCISE FUEL RACK ENGINE AIR RUN NO WATER LEAK ENGINE STANDBY WAITING FOR DISPATCH | ENGINE OPERATOR |  | 2022-01-27 13:58:30 | Done
|  |  | 2022-01-30 07:30 | 2022-01-31 08:48:13 |  | 2022-01-30 | Undergo standard 500RH PMS. | Maintenance team, Elecl, and Operations |  | 2022-01-30 07:54:08 | Done
|  |  | 2022-01-30 10:00 | 2022-01-30 15:44:03 |  | 2022-01-30 | Pulled-out cylinder head no.2 due to exhaust valve gas cutting. the replaced with recond spare cylinder head. | Maintenance team |  | 2022-01-30 15:44:03 | Done
|  |  | 2022-01-31 08:50 | 2022-01-31 14:00:39 |  | 2022-01-31 | Pulled-out LO cooler, then replaced with recond spare | Maintenance team |  | 2022-01-31 08:51:13 | Done
|  |  | 2021-01-02 07:00 | 2022-01-31 16:49:42 |  | 2021-01-02 | 0700H ENGINE ON STANDBY 0743H LO SEPARATOR PANEL ON FEEDPUMP AND HEATER ON OPEN AIR AND WATER SUPPLY 0749H START SEPARATOR 0752H START SEPARATION 0820H STOPPING LO SEPARATOR *CHANGING OF COUPLING OF PRIMING PUMP *CLEAN FUEL FILTER BESIDES ENGINE @ RH â€“ 929 HRS 1010H LO SEPARATOR FEED PUMP @ HEATER ONLINE 1040H START SEPARATOR 1043H START SEPARATION 1045H ALARM OIL BACK PRESSURE 1052H STOPPING LO SEPARATOR 1300H LO SOUNDING 30.3 CM ENGINE OFFLINE LO SEPARATOR OFFLINE LO PRIMING OFFLINE 1900H ALARM OIL FEED TEMP TOO LOW NOTE: ONLINE LO PRIMING PUMP WHEN ENGINE BARRING AND BEFORE ENGINE START UP *EXERCISE FUEL RACK WITH OIL *ENGINE BARRING | MANPOWER: EO- VILLANUEVA AO-RAMOS, CALDERON CRO-VALDEZ |  | 2022-01-31 16:49:42 | Done
|  |  | 2022-02-13 09:00 | 2022-02-13 14:23:40 |  | 2022-02-13 | Booster module-1 HFO Differential Filter undergo cleaning/servicing. The filter was removed, then cleaned, then installed back. | Mechanical team |  | 2022-02-13 14:23:40 | Done
|  |  | 2021-02-10 : | 2022-03-08 16:25:23 |  |  | DATE: FEBRUARY 10, 2021 MANPOWER: EO-CUNANAN,LINGA AO-ARCILLA,BANASTAS CRO-CALLE SS-PANGAN ENGINE BARRING ENGINE AIR RUN : NO WATER LEAK | MANPOWER: EO-CUNANAN,LINGA AO-ARCILLA,BANASTAS CRO-CALLE SS-PANGAN |  | 2022-03-08 16:25:23 | Done
|  |  | 2021-02-11 07:00 | 2022-03-08 16:27:19 |  |  | DATE: FEBRUARY 11, 2021 MANPOWER: EO-VILLANUEVA AO-CALDERON, RAMOS CRO-VALDEZ SS-OLAGUER 0700H ENGINEON STANDBY 0750H LO SEPARATOR PANEL ON FEEDPUMP AND HEATER ONLINE 0855H STOPPING LO HEATER 0910H FEEDPUMP AND HEATER OFFLINE 1055H ENGINE START 1105H ENGINE @ 310 KW LOAD 1110H ENGINE @ 40 KW LOAD 1115H ENGINE @ 1000KW LOAD 1121H ENGINE SHUTDOWN : NO FEEDBACK POWER 1129H ENGINE TART 1139H ENGINE @ 1MW LOAD 1143H ENGINE @ 1.2 MW LOAD 1156H ENGINE SHUTDOWN GB EXTERNAL TRIP 1258H ENGINE START CHANGE OVER HFO TO LFO 1306H ENGINE NORMAL STOP | MANPOWER: EO-VILLANUEVA AO-CALDERON, RAMOS CRO-VALDEZ SS-OLAGUER |  | 2022-03-08 16:27:19 | Done
|  |  | 2021-02-11 15:00 | 2022-03-08 16:31:12 |  |  | DATE: FEBRUARY 11, 2021 MANPOWER: EO-ORNEDO AO-LEUTERIO CRO-VALDEZ,MASCULINO SS-OLAGUER,PANGAN ACTIVITIES: 1500H ENGINE IS ON STANDBY 0215H 32.3 CM (1347.9 L) ENGINE OFFLINE LO PRIMING OFFLINE LO SEPERATOR AND HEATER OFFLINE | MANPOWER: EO-ORNEDO AO-LEUTERIO CRO-VALDEZ,MASCULINO SS-OLAGUER,PANGAN |  | 2022-03-08 16:31:12 | Done
|  |  | 2021-02-01 : | 2022-03-21 17:34:20 |  |  | DATE: FEBRUARY 01,2021 MANPOWER: EO-MANIBO, CUNANAN AO-ARCILLA,BANASTAS CRO-CALLE SS-OLAGUER ACTIVITIES: 0930H ENGINE START FOR TESTING ENGINE STOP 1228H ENGINE START 1235H ENGINE TRIP(HIGH TEMP) |  |  | 2022-03-21 17:34:20 | -Select Status-
|  |  | 2020-03-08 : | 2022-03-24 15:02:57 |  |  | DATE: AUG 30, 2020 MANPOWER: RUTHER ORNEDO â€“ EO LAURENCE LINGA â€“ EO MARK RAMOS â€“ AO JUBERT CORTEZA â€“ CRO BRIAN ANI â€“ SUPERVISOR ACTIVITIES: 1. ENGINE PRIMING PUMP ONLINE 2. ENGINE BARRING 3. ENGINE AIR RUN 4. ALFA LAVAL HEATER ONLINE | MANPOWER: RUTHER ORNEDO â€“ EO LAURENCE LINGA â€“ EO MARK RAMOS â€“ AO JUBERT CORTEZA â€“ CRO BRIAN ANI â€“ SUPERVISOR |  | 2022-03-24 15:02:57 | Done
|  |  | 2020-08-31 19:00 | 2022-03-30 16:36:13 |  |  | DATE: AUGUST 31, 2020 MANPOWER: GIAN CUNANAN - EO KEVIN VILLANUEVA â€“ EO LAURENCE LINGA - EO RUTHER ORNEDO â€“ EO MARK RAMOS- AO MICHAEL MAÃ‘IBO â€“ AO JULIUS CESAR MENDOZA- AO JUBERT CORTEZA â€“ CRO ENRICO BRIAN ANI - SUPERVISOR ACTIVITIES: 1. ENGINE PRIMING PUMP ONLINE 2. ENGINE BARRING 3. ALFA LAVAL HEATER ONLINE 4. ENGINE PREPARATION 1930H ENGINE AIR-RUN 1959H ENGINE START â€¢ LOAD LIMIT â€“ 1 â€¢ SPEED SETTING â€“ 3 2000H ENGINE STOP (FAILURE: ENGINE STARTING FAIL) 2008H ENGINE START â€¢ LOAD LIMIT â€“ 4 â€¢ SPEED SETTING â€“ 3 2009H ENGINE STOP (FAILURE: OVERSPEED SHUTDOWNN) SPEED SETTING CONTROL 650 2117H ENGINE START â€¢ LOAD LIMIT â€“ 3 â€¢ SPEED SETTING â€“ 2 2132H ENGINE STOP ( FAILURE : LO LOW LEVEL SHUTDOWN) 2135H MAINTENANCE INSPECTION | MANPOWER: GIAN CUNANAN - EO KEVIN VILLANUEVA â€“ EO LAURENCE LINGA - EO RUTHER ORNEDO â€“ EO MARK RAMOS- AO MICHAEL MAÃ‘IBO â€“ AO JULIUS CESAR MENDOZA- AO JUBERT CORTEZA â€“ CRO ENRICO BRIAN ANI - SUPERVISOR |  | 2022-03-30 16:36:13 | Done
|  |  | 2020-09-01 : | 2022-03-30 16:37:38 |  |  | DATE: SEPTEMBER 01, 2020 MANPOWER: EO : G. CUNANAN, K. VILLANUEVA, L.LINGA, R. ORNEDO AO : M. RAMOS, J.MENDOZA, M.MAÃ‘IBO CRO: JUBERT CORTEZA SUPERVISOR: ENRICO BRIAN ANI ACTIVITIES: 1. ENGINE PRIMING PUMP ONLINE (4 LUBE OIL FILTER CLEANING) 2. ENGINE BARRING 3. ALFA LAVAL HEATER ONLINE 1339H AIR RUN 1348H ENGINE START 1349H ENGINE STOP ( NOTICE: OVERSPEED) 1423H ENGINE START (IDLE) 1445H ENGINE STOP (NOTICE F.O HIGH LEVEL ALARM) 1453H ENGINE INSPECTION â€“ MAINTENANCE TEAM 1631H ENGINE START (IDLE) 1708H ENGINE STOP (NOTICE F.O HIGH LEVEL ALARM) 1853H ENGINE AIR RUN 1910H ENGINE START 2022H ENGINE STOP (NOTICE:JACKET WATER TEMP TOO HIGH ) 2125H ENGINE INSPECTION â€“ MAINTENANCE TEAM 2208H ENGINE AIR RUN 2211H ENGINE START 2230H ENGINE STOP 2232H ENGINE START 2244H ENGINE STOP (NOTICE: SPEED SENSOR FAIL) 2247H ENGINE INSPECTION | MANPOWER: EO : G. CUNANAN, K. VILLANUEVA, L.LINGA, R. ORNEDO AO : M. RAMOS, J.MENDOZA, M.MAÃ‘IBO CRO: JUBERT CORTEZA SUPERVISOR: ENRICO BRIAN ANI |  | 2022-03-30 16:37:38 | Done
|  |  | 2020-09-02 07:00 | 2022-03-30 16:39:33 |  |  | DATE: SEPTEMBER 02, 2020 MANPOWER: EO- L.LINGA, R.ORNEDO,K.VILLANUEVA AO- M.RAMOS, J.MENDOZA CRO- JUBERT CORTEZA ACTIVTIES: 1. ENGINE PRIMING PUMP ONLINE 2. ENGINE BARRING 3. ALFA LAVAL HEATER ONLINE 4. LUBE OIL FILTER CLEANING 1051H AIR BLOW 1059H STARTED 1155H ENGINE STOP 1230H ENGINE START 1245H RATED 1301H ENGINE STOP 1325H ENGINE START 1331H RATED 1414H ENGINE STOP 1520H ENGINE START 1525H ENGINE RATED 1533H ENGINE STOP 1546H ENGINE START 1549H ENGINE RATED 1600H ENGINE 500KW LOAD 1717H ENGINE STOP 1720H INSPECTION â€“ MAINTENANCE TEAM 1824H ENGINE AIR RUN 1827H ENGINE STARTED 1856H ENGINE RATED 1847H ENGINE 500KW LOAD 1900H ENGINE 1000KW LOAD 1931H ENGINE STOP â€“ ELECTRIC COMMON TRIP 1935H ENGINE INSPECTION LUBE OIL SOUNDING : @500KW = 1226L @1000KW = 1325L 2135H AIR RUN 2136H ENGINE START 2142H ENGINE RATED 2149H ENGINE 1000KW LOAD 2218H SOUNDING LUBE OIL â€“ 1205L 2227H ENGINE LOAD 1500KW 2232H ENGINE 1300KW LOAD 2233H SOUNDING LUBE OIL 1093L 2311H ENGINE STOP | MANPOWER: EO- L.LINGA, R.ORNEDO,K.VILLANUEVA AO- M.RAMOS, J.MENDOZA CRO- JUBERT CORTEZA |  | 2022-03-30 16:39:33 | Done
|  |  | 2020-09-03 12:00 | 2022-03-30 16:41:49 |  |  | DATE: SEPTEMBER 03, 2020 MANPOWER: EO-L.LINGA, R.ORNEDO, K.VILLANUEVA AO-M.RAMOS,J.MENDOZA CRO-JUBERT CORTEZA ACTIVITES: 1. ENGINE PRIMING PUMP ONLINE 2. ENGINE BARRING 3. ALFA LAVAL HEATER ONLINE 4. LUBEOIL FILTER CLEANING 1253H ENGINE AIR RUN 1302H ENGINE START 1323H ENGINE @ 500KW 1335H ENGINE @1MW 1412H ENGINE @1.5MW 1433H ENGINE STOP 1450H MAINTENANCE INSPECTION 1628H ENGINE AIR RUN 1632H ENGINE START 1640H ENGINE RATED SPEED 1649H GEN. SYNCHRONIZED TO BUS 1650H ENGINE @ 500KW 1703H ENGINE @ 1000KW 1740H ENGINE @ 1400KW 2034H REDUCE LOAD 2039H ENGINE @ 1000KW, CHANGE OVER HFO TO LFO 2133H VCB OPEN 2134H ENGINE STOP â€“ LUBE OIL LEVEL @ 32.2 CM | MANPOWER: EO-L.LINGA, R.ORNEDO, K.VILLANUEVA AO-M.RAMOS,J.MENDOZA CRO-JUBERT CORTEZA |  | 2022-03-30 16:41:49 | Done
|  |  | 2020-09-03 : | 2022-03-30 16:43:18 |  |  | DATE: SEPTEMBER 03, 2020 MANPOWER: EO- K.VILLANUEVA, L.LINGA AO- J.MENDOZA CRO-JUBERT CORTEZA ASST.TD: R. LOPEZ ACTIVITIES: 0720H ENGINE PRIMING STOP 0725H MECHANICAL TEAM INSPECTION 0840H ENGINE PRIMING RUNNING 0846H ENGINE BARRING 0941H ENGINE AIR RUN 1006H ENGINE START 1007H ENGINE STOP 1008H ENGINE START 1009H STOP ENGINE 1012H START ENGINE 1027H ENGINE STOP 1050H ENGINE START 1058H ENGINE RATED 1051H ENGINE RATED 1105H ENGINE 500KW LOAD @ L.L. 2.4 1120H ENGINE 1000KW LOAD @ L.L 3.6 1130H CHANGE OVER FROM LFO TO HFO 1140H ENGINE LOAD 1400KW 1300H PMAX 1330H ADJUSTIBF FUEL RACK OPENING CYLINDER NO. 6 1440H ENGINE SHUTDOWN ; NO FEEDBACK POWER 1445H INSPECTION 1625H FLUSHING OF DIESEL (LFO) 1628H AIR RUN 1630H START FAIL 1632H START FAIL 1633H ENGINE START 1642H ENGINE RATED 1647H ENGINE 500 KW LOAD 1655H ENGINE 1000 KW LOAD 1657H CHANGE OVER FROM LFO TO HFO 1722H ENGINE 1400KW LOAD 2130H TURN OVER | MANPOWER: EO- K.VILLANUEVA, L.LINGA AO- J.MENDOZA CRO-JUBERT CORTEZA ASST.TD: R. LOPEZ |  | 2022-03-30 16:43:18 | Done
|  |  | 2020-09-09 : | 2022-04-01 11:30:05 |  |  | DATE: SEPTEMBER 09, 2020 MANPOWER: EO- GIAN CUNANAN, RUTHER AO- MICHAEL MAÃ‘IBO, MARK RAMOS CRO-JUBERT CORTEZA 1120H ENGINE TRIP DUE TO LINE FAULT 1320H ENGINE START 1321H ENGINE RATED 900 RPM 1340H CHANGE OVER TO HFO (1000 KW) 1200H LO SOUNDING 28.8 (1231 LITERS) 1800H LO SOUNDING 28.5 (1221 LITERS) ENGNE RUNNING NOTE: LEAK, CRANKCASE RELIEF COVER (EXHAUST SIDE NO2) | MANPOWER: EO- GIAN CUNANAN, RUTHER AO- MICHAEL MAÃ‘IBO, MARK RAMOS CRO-JUBERT CORTEZA |  | 2022-04-01 11:30:05 | Done
|  |  | 2020-09-09 19:00 | 2022-04-01 11:31:25 |  |  | DATE:SEPTEMBER 09, 2020 1900H â€“ TURN OVER 1925H â€“ ENGINE LOAD @ 1000 KW 1927H CHANGE OVER FROM HFO TO LFO 1937H ENGINE NORMAL STOP DUE TO LOW DEMAND SOUNDING : 1238L (PRE-LUB PUMP NOT RUNNING) | MANPOWER: EO- KEVIN, LAURENCE LINGA AO-JULIUS MENDOZA CRO- RANDY, JUBERT CORTEZA |  | 2022-04-01 11:31:25 | Done
UPDATES: |  |  | : | [6 empty] | 2022-04-01 11:45:25 | Done
|  |  | 2020-10-09 15:00 | 2022-04-01 11:33:13 |  |  | DATE:SEPTEMBER 10, 2020 ACTIVITIES: CLEANING OF LUBE OIL FILTERS CLEANING OF FUEL FILTERS TIGHTENING OF BOLTS NOTE: UNDER MAINTENANCE CYLINDER FOR WATER LEAKING 1655H â€“ LO SOUNDING 27.5CM (1188 LITERS) PRE-LUB PUMP RUNNING 1755H â€“ AIR BLOW 1758H â€“ RUNNING 1800H SOUNDING 25.6 CM (1124 LITERS) ENGINE RUNNING 1815H STOP DUE TO TRIP HIGH TEMP JACKET WATER NOTE: UNDER MAINTENANCE LT HT IN/ OUT | MANPOWER: EO- GIAN CUNANAN, RUTHER ORNEDO AO- MICHAEL MAÃ‘IBO. MARK RAMOS CRO- JUBERT CORTEZA |  | 2022-04-01 11:33:13 | Done
|  |  | 2020-10-09 19:00 | 2022-04-01 11:35:45 |  |  | DATE:SEPTEMBER 10, 2020 ACTIVTIES: 1900H â€“ TURN OVER CONTINUE MAINTENANCE OF HT MECHANISM THERMOSTAT 2015H â€“ ALFA LAVAL SEPARATOR ONLINE 2130H â€“ DONE H.T COMPONENT MAINTENANCE 0627H â€“ ENGINE AIR RUN 0629 H â€“ ENGINE AIR RUN 0631H- ENGINE AIR RUN 0634H â€“ ENGINE START 0643H â€“ ENGINE @ RATED 900 RPM 0645H- ALFA LAVAL SAPARATOR STOP | MANPOWER: EO- KEVIN, LAURENCE LINGA AO-JULIUS MENDOZA CRO- RANDY, JUBERT CORTEZA |  | 2022-04-01 11:35:45 | Done
|  |  | 2022-03-23 23:00 | 2022-04-04 09:00:37 |  | 2022-03-23 | Replacement of DG2 LO filter. ERH=5074.5 | 3rd shift operations personnel |  | 2022-04-04 09:00:37 | Done
|  |  | 2022-04-04 08:00 | 2022-04-04 11:42:14 |  |  | Replacement of charge air cooler. Problem: High charge air temperature readings | Mechanical team |  | 2022-04-04 09:17:34 | Done
|  |  | 2022-04-06 07:30 | 2022-04-09 08:27:32 |  | 2022-04-06 | Conducted standard 500RH PMS to the main engine, generator, and auxiliaries | Mechanical, Electrical, Operations |  | 2022-04-06 08:46:56 | Done
|  |  | 2022-04-06 08:30 | 2022-04-09 08:27:48 |  | 2022-04-06 | Repair/welding works of a cracked portion of Turbocharger adaptor connecting turbocharger and smokestack. | Nestor Beato |  | 2022-04-06 08:50:56 | Done
|  |  | 2020-11-09 07:00 | 2022-04-06 16:09:06 |  |  | SEPT.11, 2020 0718H â€“ ENGINE STOP 0817H â€“ AIR BLOW 0823H â€“ START ENGINE 0836H â€“ CHANGE OVER 0840H- 1.4 MW 1200H â€“ SOUNDING 27.1 CM (1174 LITERS) ENGINE RUNNING NOTE: EXHAUST AFTER TURBO NEAR BELLOWS (NUT AND WASHER LOOSE) |  |  | 2022-04-06 16:09:06 | Done
|  |  | 2020-11-09 19:00 | 2022-04-06 16:10:33 |  |  | DATE:SEPTEMBER 11, 2020 ACTIVITIES: 1900H - TURN OVER ENGINE STILL RUNNING @1400 KW LOAD LO SOUNDING 27 CM = 1171 LITERS 0035H â€“ FIRING PRESSURE WITH FUEL RACK SCALE C1- 148 @23 C4- 150 @23 C7-130@23 C2- 150@23 C5- 142@23 C8- 150@23 C3-140@24 C6- 144@23 C9- 148@23 LO SOUNDING WHILE ENGINE RUNNING 26.8 CM (1164LITERS) NOTE: LO LEAK ON CYLINDER NO8 AND 6 EXHAUST SIDE LO LEAK ON CRANKCASE RELIEF VALVE 0600H â€“ LO SOUNDING WHILE ENGINE RUNNING 26.4 CM (1151 L ) | MANPOWER: EO- KEVIN VILLANUEVA AO-JULIUS MENDOZA CRO- JUBERT CORTEZA |  | 2022-04-06 16:10:33 | Done
|  |  | 2020-12-09 07:00 | 2022-04-06 16:12:18 |  |  | DATE: SEPTEMBER 12, 2020 MANPOWER: EO- GIAN CUNANAN, LAURENCE LINGA AO- MARK RAMOS CRO- DANNY MASCULINO ACTIVITIES: 0880H *NOTE ADD ENGINE OIL 209 L 1200H LUBE OIL SOUNDING 33.1 CM ==1371 L 1548H TRIP 24MH4 OPEN 1720H ENGINE START 1740H ENGINE LOAD 700 KW 1800H LO SOUNDING 32 CM | EO- GIAN CUNANAN, LAURENCE LINGA |  | 2022-04-06 16:12:18 | Done
|  |  | 2020-12-09 19:00 | 2022-04-06 16:13:55 |  |  | DATE: SEPTEMBER 12, 2020 MANPOWER: EO â€“ KEVIN, VILLANUEVA AO- MICHAEL MAÃ‘IBO CRO â€“ JUBERT CORTEZA ACTIVTIES: 1928H CHANGE OVER FROM HFO TO LFO 1937H ENGINE NORMAL STOP 2230H ENGINE AIR RUN 2233H ENGINE START 2243H ENGINE @ RATED 900RPM 2253H ENGINE @ 500 KW LOAD 2308H ENGINE @1000 KW LOAD 2309H CHANGE OVER FROM LFO TO HFO 2318H ENGINE @1400 KW LOAD 0047H ENGINE NORMAL STOP *CLEANED TURBO CHARGER FILTER 0600H LO SOUNDING WHILE ENGINE PRIMING RUNNING 31.7 CM = 1328 LITERS | EO â€“ KEVIN, VILLANUEVA |  | 2022-04-06 16:13:55 | Done
|  |  | 2022-04-08 19:45 | 2022-04-09 08:26:53 |  | 2022-04-08 | 24MH4 MV Circuit Breaker supplying Pi101 manually open/isolated. Pi101 load transferred to Pi100 after energization of Pinamalayan 10MVA substation. MHEC is now operating and supplying a 69kV line only. | 2nd shift CRO |  | 2022-04-09 08:26:53 | Done
|  |  | 2022-04-29 23:00 | 2022-04-30 06:26:05 |  | 2022-04-30 | Change tap 15MVA Trafo from tap-4 to tap-3 (13.8/4.16kV) | EIC and Bong Latoza |  | 2022-04-30 06:26:05 | Done
UPDATES: |  |  | 2022-05-17 : |  |  |  | Change tap again. Revert from Tap-3 to Tap-4 | EIC and Bong Latoza |  | 2022-05-17 13:35:31 | Done
|  |  | 2022-04-29 23:00 | 2022-04-30 06:27:12 |  | 2022-04-30 | Replacement of DG1 cyl head #4 due to gas cut | Mechanical team |  | 2022-04-30 06:27:12 | Done
|  |  | 2022-04-30 11:57 | 2022-05-02 06:51:27 |  |  | DG3 Cooling tower fan bearing is defective and undergoes CMS | Mechanical team |  | 2022-05-02 06:51:27 | Done
UPDATES: |  |  | 2022-05-10 16:49 |  |  |  | The cooling tower fan has already been rectified by the mechanical team. The defective bearing was replaced by a modified bearing (inner hole binawasan) just to fit in the cooling fan shafting. | Mechanical team |  | 2022-05-10 16:52:31 | Done
|  |  | 2022-06-07 07:30 | 2022-06-08 09:18:00 |  | 2022-06-07 | Conducted CMS to DG4: Pull-out and replaced engine-driven fuel pump. | Mechanical team |  | 2022-06-08 09:18:00 | Done
|  |  | 2022-06-08 08:00 | 2022-06-08 11:09:34 |  | 2022-06-08 | LOP-1 heater elements undergo cleaning/servicing. | EIC |  | 2022-06-08 11:09:34 | Done
|  |  | 2022-06-21 13:00 | 2022-06-22 11:18:41 |  | 2022-06-21 | Pull out defective Basler AVC125 AVR and replaced it with Basler SSR125-12 AVR from Calapan spare AVR. Test run the unit, performed load test up to 1.4MW for 1 hour. -Successful | ECMG and EIC |  | 2022-06-22 11:18:41 | Done
|  |  | 2022-07-07 09:08 | 2022-07-20 08:39:23 |  | 2022-07-07 | Qualified for 400 RH servicing of Mitsubishi SJ30F HFO #2 (Total RH = 2695.3 RH) | Mark Ramos; Warren Bequilla; Joey Agoncillo |  | 2022-07-20 08:39:23 | Done
UPDATES: |  |  | 2022-07-07 07:00 |  |  |  | Qualified for 400 RH servicing of Mitsubishi SJ30F HFO #2 (Total RH = 2695.3 RH) 1. Cleaning of gravity disk. 2. Pairing chamber. 3. Housekeeping in the HFOP area. | Mark Ramos; Warren Bequilla; Joey Agoncillo |  | 2022-07-20 08:43:33 | Done
|  |  | 2022-07-09 07:30 | 2022-07-20 08:48:38 |  | 2022-07-11 | HIMSEN 9H21/32 DG#2 lube oil temperature display at the control room panel is in "open" signal | Aldo Marcelino; Jaylord Delica |  | 2022-07-20 08:48:38 | Done
UPDATES: |  |  | 2022-07-09 07:30 |  |  |  | HIMSEN 9H21/32 DG#2 lube oil temperature display at the control room panel is in "open" signal 1. Wire tracing 2. Troubleshooting 3. Re-connect and rewiring | Aldo Marcelino; Jaylord Delica |  | 2022-07-20 08:51:48 | Done
|  |  | 2022-07-11 07:30 | 2022-07-20 08:56:07 |  | 2022-07-11 | HIMSEN 9H21/32 DG#2 won't start. The "Ready to Start" indicator won't lit. | Jestoni Reforma; Aldo Marcelino |  | 2022-07-20 08:56:07 | Done
UPDATES: |  |  | 2022-07-11 07:30 |  |  |  | HIMSEN 9H21/32 DG#2 won't start. The "Ready to Start" indicator won't lit. Action: Troubleshoot wiring from relay K2 to relay K1. Timer T1 activated to lit relay K1. Need an as-built diagram for maintenance to troubleshoot the problem more easily. | Jestoni Reforma; Aldo Marcelino |  | 2022-07-20 09:03:11 | Done
|  |  | 2022-07-01 07:30 | 2022-07-20 09:06:45 |  | 2022-07-01 | Wiper is not working | Aldo Marcelino; Maximo Marasigan |  | 2022-07-20 09:06:45 | Done
UPDATES: |  |  | 2022-07-01 07:30 |  |  |  | Wiper is not working 1. Wire tracing 2. Troubleshooting from motor wiper up to the terminal fuse. | Aldo Marcelino; Maximo Marasigan |  | 2022-07-20 09:08:38 | Done
|  |  | 2022-07-01 01:00 | 2022-07-20 09:10:09 |  | 2022-07-01 | Ignition/Starter switch is not working | Aldo Marcelino; Maximo Marasigan |  | 2022-07-20 09:10:09 | Done
UPDATES: |  |  | 2022-07-01 01:30 |  |  |  | The ignition/starter switch is not working. Action taken: 1. Wire tracing 2. Troubleshooting from the starter up and selector switch ignition. Parts replaced: 1. 10 mtr/s of Automative wire #14 2. 5 pc/s of fuse plug-in type | Aldo Marcelino; Maximo Marasigan |  | 2022-07-20 09:13:44 | Done
|  |  | 2022-07-17 07:00 | 2022-07-20 09:17:17 |  | 2022-07-17 | Continuous backwash showing high differential pressure filter of BoosterModule #1. | Warren Bequilla; Joey Agoncillo |  | 2022-07-20 09:17:17 | Done
UPDATES: |  |  | 2022-07-17 07:00 |  |  |  | Continuous backwash showing high differential pressure filter of BoosterModule #1. Action taken: 1. Dismantle element. 2. Cleaning the element. 3. Re-installed the element. 4. Testing backwash filter on booster module #1 after service. | Warren Bequilla; Joey Agoncillo |  | 2022-07-20 09:19:14 | Done
|  |  | 2022-07-15 07:30 | 2022-07-20 09:22:10 |  | 2022-07-15 | The temperature reading on the settling tank heater goes up to 300 Deg Celsius which is abnormal. | Aldo Marcelino |  | 2022-07-20 09:22:10 | Done
UPDATES: |  |  | 2022-07-15 07:30 |  |  |  | The temperature reading on the settling tank heater goes up to 300 Deg Celsius which is abnormal. Action taken: 1. Inspection of wiring connectors on L3. 2. Conduct IR testing. 3. Conduct multitester testing. 4. Re-tightening of the bolt inside the panels. 5. Cleaning of the panels. Parts replaced: 1. 1 mtr of #8 wire | Aldo Marcelino |  | 2022-07-20 09:26:36 | Done
|  |  | 2022-07-18 07:30 | 2022-07-21 09:07:06 |  | 2022-07-18 | There is smoke coming out from the Mitsubishi SJ30F HFO#1. | Aldo Marcelino; Jaylord Delica; Joy Ecal; Jakeson Lastica |  | 2022-07-21 09:07:06 | Done
UPDATES: |  |  | 2022-07-18 07:30 |  |  |  | There is smoke coming out from the Mitsubishi SJ30F HFO#1. Action taken: 1. Dismantle HFO#1 motor 2. Replaced friction block 60Hz. 3. Re-installed. Testing of the equipment. Parts replaced: 1. 3 pc/s of friction block/clutch 60Hz | Aldo Marcelino; Jaylord Delica; Joy Ecal; Jakeson Lastica |  | 2022-07-21 09:09:35 | Done
|  |  | 2022-07-01 08:00 | 2022-07-23 08:27:01 |  | 2022-07-03 | Problem/Findings: To check cylinder heads nos. 4 and 6 due to suspected diesel contamination at the rocker's arm. | Joy Ecal; Jakeson Lastica; Joey Agoncillo; Nestor Beato; Warren Bequilla |  | 2022-07-23 08:27:01 | Done
UPDATES: |  |  | 2022-07-03 07:20 |  |  |  | Problem/Findings: To check cylinder heads nos. 4 and 6 due to suspected diesel contamination at the rocker's arm. Action Taken: 1. Pulled out nozzle cooling pipe on cylinders nos. 4 and 6. 2. Replaced new copper gaskets. 3. Replaced stud bolt of cylinder heads cover. 4. Ready for testing and housekeeping. Parts Replaced: 1. 4 pcs of copper gaskets ID: 14.00 mm; OD: 19.50 mm; t: 2 mm 2. 8 pcs of copper gaskets ID: 14.30 mm; OD: 21.85 mm; t: 1 mm 3. 2 pcs of Adapter (E326273280Z) | Ramir T. Radaza; Joy Ecal; Jakeson Lastica; Joey Agoncillo; Nestor Beato; Warren Bequilla |  | 2022-07-23 08:39:46 | Done
|  |  | 2022-07-24 07:00 | 2022-07-25 07:12:56 |  | 2022-07-25 | Problem/Findings: High Exhaust Gas Temperature (EGT) on Cylinder no. 5. Work Description: For mechanical inspection. For electrical temperature gauge calibration. | Ramir T. Radaza; Jestoni Reforma |  | 2022-07-25 07:12:56 | Done
UPDATES: |  |  | 2022-07-25 07:00 |  |  |  | N/A | Ramir T. Radaza; Joy Ecal; Jakeson Lastica; Warren Bequilla; Mark Ramos |  | 2022-07-27 15:21:30 | Done
|  |  | 2022-07-24 07:00 | 2022-07-25 07:14:50 |  | 2022-07-25 | Problem/Findings: No Indication for Ready To Start. Work Description: For electrical inspection. | Jestoni Reforma; Zeus Delica |  | 2022-07-25 07:14:50 | Done
UPDATES: |  |  | 2022-07-25 19:00 |  |  |  | Problem/Findings: No Indication for Ready To Start. Action Taken: 1. Checked all wiring connections. 2. Checked loose contacts if still okay. 3. Re-set all alarms. 4. Back all switches to normal operation. | Jestoni Reforma; Aldo Marcelino |  | 2022-07-26 13:32:31 | Done
|  |  | 2022-07-24 07:00 | 2022-07-25 07:16:41 |  | 2022-07-25 | Equipment Type/Model: Alfa Laval LOP#2 Problem/Findings: Heater Fault Alarm Work Description: For electrical inspection | Jestoni Reforma; Zeus Delica |  | 2022-07-25 07:16:41 | Done
UPDATES: |  |  | 2022-07-25 08:00 |  |  |  | Equipment Type/Model: Alfa Laval LOP#2 Problem/Findings: Heater Fault Alarm Action Taken: 1. Re-set LOP#2 controller. 2. Check some wiring connections. 3. Monitor while starting. Reminder to all operators from EIC maintenance team: Don't start the separation process while the temperature is low. The starting temperature should be 60-85 deg Celcius. | Jestoni Reforma; Aldo Marcelino |  | 2022-07-26 13:37:55 | Done
|  |  | 2022-07-25 11:00 | 2022-07-25 11:06:49 |  | 2022-07-26 | Problem/Findings: The serpentine belt of Mitsubishi L300 was derailed. Work Description: For mechanical inspection. | Ramir T. Radaza |  | 2022-07-25 11:06:49 | Done
UPDATES: |  |  | 2022-07-25 : |  |  |  | The serpentine belt of Mitsubishi L300 was derailed. |  |  | 2022-07-25 11:33:33 | On-Progress
UPDATES: |  |  | 2022-07-26 13:00 |  |  |  | N/A | Joy Ecal; Warren Bequilla |  | 2022-07-27 15:28:36 | Done
UPDATES: |  |  | 2022-07-26 13:00 |  |  |  | Ready to operate. | Joy Ecal; Warren Bequilla |  | 2022-07-26 | Done
UPDATES: |  |  | 2022-07-26 13:00 |  |  |  | N/A | Joy Ecal; Warren Bequilla |  | 2022-08-04 09:45:45 | Done
|  |  | 2022-07-26 : | 2022-07-26 08:08:52 |  | 2022-07-29 | 1. Qualified for standard 400RHS Servicing. (Total = 7,322.00 RH); 2. Change Oil (Shell Omalla Gx150) |  |  | 2022-07-26 08:08:52 | Done
UPDATES: |  |  | 2022-08-03 08:00 |  |  |  | Ready to operate. | Aldo Marcelino; Jaylord Delica; Mark Ramos; Jakeson Lastica |  | 2022-08-12 08:45:17 | Done
|  |  | 2022-07-26 : | 2022-07-26 08:10:16 |  | 2022-07-29 | 1. Qualified for 400RHS Servicing. (Total = 5,802.00 RH); 2. Change Oil (Shell Omalla Gx150) |  |  | 2022-07-26 08:10:16 | Done
UPDATES: |  |  | 2022-07-27 08:00 |  |  |  | Waiting for electrical service report. | Mark Ramos; Jakeson Lastica |  | 2022-07-27 | On-Progress
UPDATES: |  |  | 2022-07-26 08:00 |  |  |  | Ready to operate. | Mark Ramos; Jakeson Lastica; Jestoni Reforma; Aldo Marcelino |  | 2022-08-04 10:09:07 | Done
|  |  | 2022-07-26 : | 2022-07-26 08:11:56 |  | 2022-07-29 | Alfa Laval no. 5 qualified for 2000 RHS servicing. (Total = 1920 RH) |  |  | 2022-07-26 08:11:56 | Done
UPDATES: |  |  | 2022-07-26 08:00 |  |  |  | N/A | Jestoni Reforma; Aldo Marcelino |  | 2022-07-28 08:26:53 | On-Progress
UPDATES: |  |  | 2022-07-28 08:00 |  |  |  | N/A | Mark Ramos; Jakeson Lastica |  | 2022-07-28 | On-Progress
UPDATES: |  |  | 2022-07-26 08:00 |  |  |  | Ready to operate. | Mark Ramos; Jakeson Lastica; Jestoni Reforma; Aldo Marcelino |  | 2022-07-28 | Done
UPDATES: |  |  | 2022-07-26 08:00 |  |  |  | Ready to operate. | Mark Ramos; Jakeson Lastica; Jestoni Reforma; Aldo Marcelino |  | 2022-07-28 | Done
|  |  | 2022-07-26 : | 2022-07-26 08:21:49 |  | 2022-07-29 | Monthly (standard) Preventive Maintenance Schedule (PMS) of SPERRE 1 & 2. |  |  | 2022-07-26 08:21:49 | Done
UPDATES: |  |  | 2022-07-28 08:00 |  |  |  | EIC: Compressor is not running in automatic mode. Need for some checking and inspection. | Aldo Marcelino; Jaylord Delica; Mark Ramos |  | 2022-08-09 08:04:49 | Done
|  |  | 2022-07-26 : | 2022-07-26 08:23:01 |  | 2022-07-29 | Monthly (standard) Preventive Maintenance Schedule (PMS) of Armstrong air compressor. |  |  | 2022-07-26 08:23:01 | Done
UPDATES: |  |  | 2022-07-28 08:00 |  |  |  | N/A | Aldo Marcelino; Jaylord Delica; Mark Ramos |  | 2022-08-09 08:14:57 | Done
|  |  | 2022-07-26 : | 2022-07-26 08:23:46 |  | 2022-07-29 | Monthly (standard) Preventive Maintenance Schedule (PMS) of Kubota engine-driven air compressor. |  |  | 2022-07-26 08:23:46 | Done
UPDATES: |  |  | 2022-07-28 08:00 |  |  |  | N/A | Aldo Marcelino; Jaylord Delica; Mark Ramos |  | 2022-08-09 08:10:07 | Done
|  |  | 2022-07-17 : | 2022-07-26 08:29:23 |  | 2022-07-18 | Alfa Laval no. 2 qualified for 400 RH servicing and testing of the heater. (Total = 6774.00 RH). | Aldo Marcelino; Jaylord Delica |  | 2022-07-26 08:29:23 | Done
UPDATES: |  |  | 2022-07-18 08:12 |  |  |  | Problem/Findings: Alfa Laval Lube Oil no. 2 qualified for 400 RH servicing and testing of the heater. (Total = 6774.00 RH). Action Taken: 1. Servicing of the lube oil control panel. 2. Cleaning and inspection of the lube oil control panel. 3. Tightening of control panel terminals. 4. Cleaning of the heater. 5. Insulation test of lube oil purifier heater and motors. | Aldo Marcelino; Jaylord Delica |  | 2022-07-26 08:33:04 | Done
|  |  | 2022-07-27 14:00 | 2022-07-27 08:16:29 |  | 2022-08-01 |  | Ramir T. Radaza |  | 2022-07-27 08:16:29 | Done
UPDATES: |  |  | 2022-08-03 08:00 |  |  |  | Ready to operate. | Aldo Marcelino; Jaylord Delica; Mark Ramos; Jakeson Lastica |  | 2022-08-25 13:08:39 | Done
|  |  | 2022-07-29 : | 2022-07-29 06:39:31 |  | 2022-07-29 | Noted and with clearance from sir Ramir |  |  | 2022-07-29 06:39:31 | Done
UPDATES: |  |  | 2022-07-29 07:00 |  |  |  | Ready to operate. | Joy Ecal; Jakeson Lastica; Joey Agoncillo |  | 2022-08-04 10:14:56 | Done
|  |  | : |  |  | 2022-07-31 |  | Ramir TR. Radaza |  | 2022-07-29 08:11:45 | Done
UPDATES: |  |  | 2022-07-29 08:00 |  |  |  | Ready to operate. | Joy Ecal; Jakeson Lastica; Joey Agoncillo; Nestor Beato; Warren Bequilla |  | 2022-07-29 | -Select Status-
UPDATES: |  |  | 2022-07-29 07:20 |  |  |  | Turn over to operation. For lube oil topping up (3 drums were already top-up). Ready for testing. | Ramir T. Radaza; Joy Ecal; Jakeson Lastica; Joey Agoncillo; Nestor Beato; Warren Bequilla |  | 2022-08-01 | On-Progress
UPDATES: |  |  | 2022-07-29 07:00 |  |  |  | Turn over to operation. For lube oil topping up (3 drums were already top-up). Ready for testing. | Ramir T. Radaza; Joy Ecal; Jakeson Lastica; Joey Agoncillo; Nestor Beato; Warren Bequilla |  | 2022-08-04 10:28:52 | Done
|  |  | : |  |  | 2022-07-30 |  | Ramir T. Radaza |  | 2022-07-29 08:13:06 | Done
UPDATES: |  |  | 2022-07-29 07:00 |  |  |  | No leak was found. | Ramir T. Radaza |  | 2022-08-17 14:36:47 | Done
|  |  | : |  |  | 2022-08-09 |  | Ramir T. Radaza |  | 2022-08-02 11:23:15 | Done
UPDATES: |  |  | 2022-08-02 13:10 |  |  |  | Ready to operate. | Ramir T. Radaza; Junell Magora |  | 2022-08-04 10:21:53 | Done
|  |  | : |  |  | 2022-08-04 |  | Ramir T. Radaza; Jestoni Reforma |  | 2022-08-02 11:27:11 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2022-08-26 15:26:41 | -Select Status-
|  |  | : |  |  | 2022-08-06 |  | Aldo Marcelino |  | 2022-08-06 13:44:41 | Done
UPDATES: |  |  | 2022-08-06 15:15 |  |  |  | N/A | Aldo Marcelino |  | 2022-08-09 08:34:30 | Done
|  |  | : |  |  | 2022-08-07 |  | Aldo Marcelino |  | 2022-08-06 13:47:24 | Done
UPDATES: |  |  | 2022-08-06 07:30 |  |  |  | Rectified | Aldo Marcelino; Jaylord Zeus Delica |  | 2022-08-09 08:45:21 | Done
|  |  | : |  |  | 2022-08-06 |  | Aldo Marcelino |  | 2022-08-06 13:50:30 | Done
UPDATES: |  |  | 2022-08-05 11:00 |  |  |  | Founded that transformer burn out and need to replace with new one. | Aldo Marcelino; Jaylord Delica |  | 2022-08-12 08:58:04 | Done
|  |  | : |  |  | 2022-08-08 |  | Aldo Marcelino; Zeus Delica |  | 2022-08-06 15:54:24 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2022-08-27 08:48:37 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2022-08-27 08:49:01 | -Select Status-
|  |  | : |  |  | 2022-08-07 |  |  |  | 2022-08-08 07:48:29 | Done
UPDATES: |  |  | : | [6 empty] | 2022-08-08 07:52:31 | On-Progress
UPDATES: |  |  | 2022-08-07 07:30 |  |  |  | The "Ready to start" indicator is already displayed. | Aldo Marcelino |  | 2022-08-12 09:05:03 | Done
|  |  | : | [6 empty] | 2022-08-08 07:56:41 | Done
UPDATES: |  |  | 2022-08-09 13:30 |  |  |  | Ready to operate. | Joy Ecal; Mark Ramos |  | 2022-08-20 09:55:26 | Done
|  |  | : | [6 empty] | 2022-08-08 08:37:16 | Done
UPDATES: |  |  | 2022-08-06 15:30 |  |  |  | Engine ready to start. | Nestor Beato; Warren Bequilla; John Jaraza |  | 2022-08-12 08:52:16 | Done
|  |  | 2022-08-06 : | 2022-08-08 05:14:03 |  |  | DG5 Lube Oil Purifier (LOP5) Parameter 147 has been changed from CLARIFIER to PURIFIER | Mark Ramos and buddy |  | 2022-08-08 11:14:03 | Done
|  |  | : |  |  |  | To be shutdown tonight. To be swap to DG4 after DG4 LO filter replacement. |  |  | 2022-08-08 14:55:58 | Done
UPDATES: |  |  | 2022-08-09 07:30 |  |  |  | Done. Ready to operate. | Joy Ecal; Joey Agoncillo; John Jaraza; Nestor Beato; Warren Bequilla; Mark Ramos |  | 2022-08-20 10:14:12 | Done
|  |  | : |  |  | 2022-08-13 |  | Jestoni Reforma; Aldo Marcelino |  | 2022-08-09 08:48:36 | Done
UPDATES: |  |  | 2022-08-09 08:00 |  |  |  | Ready to operate. | Jestoni Reforma; Aldo Marcelino |  | 2022-08-25 13:28:33 | Done
|  |  | : |  |  | 2022-08-13 |  | Mark Ramos; Joey Agoncillo |  | 2022-08-10 08:10:43 | Done
UPDATES: |  |  | 2022-08-10 07:30 |  |  |  | Done | Aldo Marcelino; Jaylord Delica; Mark Ramos; Joey Agoncillo |  | 2022-08-25 14:01:48 | Done
|  |  | : |  |  | 2022-08-12 |  |  |  | 2022-08-10 08:13:31 | Done
UPDATES: |  |  | 2022-08-10 07:00 |  |  |  | Ready to operate. | Joy Ecal; Jakeson Lastica, Joey Agoncillo |  | 2022-08-20 09:44:02 | Done
|  |  | : |  |  | 2022-08-15 |  | Aldo Marcelino |  | 2022-08-12 09:08:55 | Done
UPDATES: |  |  | 2022-08-11 13:00 |  |  |  | Found out that the stator winding was damaged and the fan motor was misaligned. For request of a new set of grinder. | Aldo Marcelino |  | 2022-08-25 13:42:54 | Done
|  |  | : |  |  | 2022-08-19 |  | Ramir T. Radaza |  | 2022-08-17 14:17:05 | Done
UPDATES: |  |  | 2022-08-09 08:10 |  |  |  | Ready to operate. | Nestor Beato; John Jaraza |  | 2022-08-25 13:19:15 | Done
|  |  | : |  |  | 2022-08-19 |  | Ramir T. Radaza |  | 2022-08-17 14:18:51 | Done
UPDATES: |  |  | 2022-08-16 07:00 |  |  |  | Ready to operate. | Joy Ecal; Nestor Beato; Warren Bequilla; John Jaraza |  | 2022-08-22 14:11:33 | Done
|  |  | : | [6 empty] | 2022-08-19 05:53:40 | Done
UPDATES: |  |  | 2022-08-20 08:00 |  |  |  | N/A | Aldo Marcelino; Jaylord Delica |  | 2022-08-25 13:51:58 | Done
|  |  | : | [6 empty] | 2022-08-19 06:44:42 | Done
UPDATES: |  |  | 2022-08-19 07:30 |  |  |  | Done. Ready to operate. | Joy Ecal; Jakeson Lastica, Joey Agoncillo |  | 2022-08-25 14:22:23 | Done
|  |  | : |  |  | 2022-08-30 |  |  |  | 2022-08-20 09:25:18 | On-Progress
|  |  | : |  |  | 2022-08-30 |  |  |  | 2022-08-20 09:27:05 | Done
UPDATES: |  |  | 2022-08-17 07:00 |  |  |  | N/A | Aldo Marcelino; Jaylord Delica |  | 2022-08-25 14:12:29 | Done
|  |  | : |  |  | 2022-08-30 |  |  |  | 2022-08-20 09:28:21 | Done
UPDATES: |  |  | 2022-08-19 07:30 |  |  |  | Done. Ready to operate. | Warren Bequilla; Nestor Beato |  | 2022-08-22 14:33:56 | Done
|  |  | : |  |  | 2022-08-30 |  |  |  | 2022-08-20 09:31:57 | Done
UPDATES: |  |  | 2022-08-20 13:53 |  |  |  | N/A | Jestoni Reforma; DM Contractor |  | 2022-08-22 14:18:55 | Done
|  |  | : |  |  | 2022-08-30 |  | Jestoni Reforma |  | 2022-08-23 08:03:59 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2024-08-14 10:54:24 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2024-08-14 10:54:36 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2024-08-14 10:55:10 | -Select Status-
|  |  | : |  |  | 2022-08-30 |  | Jestoni Reforma |  | 2022-08-24 08:09:28 | On-Progress
|  |  | : |  |  | 2022-08-30 |  | Jestoni Reforma |  | 2022-08-24 08:10:59 | On-Progress
|  |  | : |  |  | 2022-08-30 |  |  |  | 2022-08-25 07:57:34 | Done
UPDATES: |  |  | 2022-09-01 : | [6 empty] | 2022-08-27 11:01:54 | Done
|  |  | : |  |  | 2022-08-30 |  | Aldo Marcelino; Jaylord Delica |  | 2022-08-25 14:24:18 | -Select Status-
UPDATES: |  |  | 2022-08-31 : | [6 empty] | 2022-08-27 11:01:29 | -Select Status-
|  |  | : | [6 empty] | 2022-08-26 14:01:05 | -Select Status-
UPDATES: |  |  | : | [6 empty] | 2022-08-26 13:53:09 | -Select Status-
|  |  | 2022-08-27 1:1 | [6 empty] | 2022-08-26 16:03:55 | -Select Status-
|  |  | 2022-08-27 2:2 | [6 empty] | 2022-08-26 16:06:34 | On-Progress
|  |  | 2022-08-31 1:2 | [6 empty] | 2022-08-27 08:53:51 | -Select Status-
|  |  | 2022-08-31 : | [6 empty] | 2022-08-27 08:59:05 | On-Progress
|  |  | 2022-09-01 1:2 | [6 empty] | 2022-08-27 08:59:23 | Done